## Single Zone DLS
Single Zone Quick Reference Guide - R-454B Ductless Systems
Indoor Unit With Wireless Remote | Outdoor Unit With Base Pan Heater | AHRI Rated Btu's Cooling @ 95F [35C] Heating @ 47F [6.3C] | SEER2 | EER2 | HSPF2 | Energy Star v6.1 Certified | Line Set Liquid x Suction | Max. Line Length | Additional Charge ≥ 25ft | Max. Lift | MCA/MOCP | Max Heating Capacity BTU's At 70F [21.1C] Indoor DB @ Max CFM |  |  | Maximum Cooling BTU's At 80F [26.7C] Indoor DB @ Max CFM
[12 empty] | @-22F [-30C] | @-4F [-20C] | @5F [-15C] | @110F [43C] | @122F [50C]
This sheet is not intended to replace the installation instructions. It is a reference guide only. Always read through the installation instructions.
Deluxe Series High Wall 1:1 Heat Pump Systems
D5FPHAH06XAK | D5CPRAH06AAK | 6,000/9,000 | 33.1 | 16.5 | 29 | YES | 1/4" x 3/8" | 82.02' | .16 Oz/Ft | 49.21' | 16A / 20A | 7500 | 10130 | 13965 | 15085 | 7892
D5FPHAH09XAK | D5CPRAH09AAK | 9,000/12,000 | 31.5 | 16 | 21 | YES | 1/4" x 3/8" | 82.02' | .16 Oz/Ft | 49.21' | 16A / 20A | 7500 | 10130 | 13965 | 15085 | 7892
D5FPHAH12XAK | D5CPRAH12AAK | 12,000/12,000 | 28 | 13.5 | 13.5 | YES | 1/4" x 3/8" | 82.02' | .16 Oz/Ft | 49.21' | 16A / 20A | 7500 | 10130 | 13965 | 15085 | 7892
D5FPHAH18XAK | D5CPRAH18AAK | 18,000/20,000 | 24.5 | 14 | 15.2 | YES | 3/8" x 5/8" | 164.04' | .32 Oz/Ft | 82.02' | 24.9A / 25A | 13532 | 20482 | 24809 | 23263 | 13286
High Wall 1:1 Deluxe Heat Pump Systems
D5FSHAH06XAK | D5CSHAH06AAK | 6,000/7,000 | 25.7 | 18 | 14.8 | YES | 1/4" x 3/8" | 82.02' | .16 Oz/Ft | 49.21' | 12A / 15A | 3180 | 5125 | 7700 | 10717 | 7571
D5FSHAH09XAK | D5CSHAH09AAK | 9,000/12,000 | 27.5 | 15.5 | 12.5 | YES | 1/4" x 3/8" | 82.02' | .16 Oz/Ft | 49.21' | 15A / 15A | 5107 | 8080 | 11500 | 11215 | 7447
D5FSHAH12XAK | D5CSHAH12AAK | 12,000/12,000 | 25.5 | 13.5 | 10.5 | YES | 1/4" x 3/8" | 82.02' | .16 Oz/Ft | 49.21' | 15A / 15A | 6278 | 9260 | 11500 | 12194 | 6490
D5FSHAH18XAK | D5CSHAH18AAK | 18,000/18,000 | 21.5 | 12.5 | 11 | YES | 1/4" x 1/2" | 98.42' | .16 Oz/Ft | 65.62' | 19A / 20A | 9356 | 15050 | 18000 | 14794 | 10590
D5FSHAH24XAK | D5CSHAH24AAK | 24,000/29,000 | 21.2 | 13 | 13.5 | YES | 3/8" x 5/8" | 164.04' | .32 Oz/Ft | 82.02' | 24.9A / 25A | 13532 | 20482 | 24200 | 23263 | 13286
D5FSHAH33XAK | D5CSHAH33AAK | 33,000/36,000 | 19.6 | 12 | 10.5 | YES | 3/8" x 3/4" | 164.04' | .32 Oz/Ft | 82.02' | 34A / 35A | 19838 | 29178 | 35000 | 32895 | 21554
High Wall 1:1 Quietcomfort Heat Pump Systems
D5FSHAH12XAJ | D5CSRAH12AAJ | 12,000/12,000 | 23.5 | 13 | 9.5 | YES | 1/4" x 3/8" | 82.02' | .16 Oz/Ft | 49.21' | 18A / 20A |  | 4374 | 7700 | 11229 | 6401
D5FSHAH09XAK | D5CSRAH09AAK | 9,000/10,000 | 26 | 14.9 | 12.5 | YES | 1/4" x 3/8" | 82.02' | .16 Oz/Ft | 49.21' | 12A / 15A |  | 7578 | 8000 | 11188 | 8230
D5FSHAH12XAK | D5CSRAH12AAK | 12,000/12,000 | 25.5 | 13.1 | 10.7 | YES | 1/4" x 3/8" | 82.02' | .16 Oz/Ft | 49.21' | 12A / 15A |  | 7175 | 8400 | 11096 | 7438
D5FSHAH18XAK | D5CSRAH18AAK | 18,000/18,000 | 23.5 | 12.8 | 10.8 | YES | 1/4" x 1/2" | 98.42' | .16 Oz/Ft | 65.62' | 18A / 20A |  | 10925 | 12800 | 14747 | 5496
D5FSHAH24XAK | D5CSRAH24AAK | 24,000/25,000 | 23.1 | 14 | 11.7 | YES | 3/8" x 5/8" | 164.04' | .32 Oz/Ft | 82.02' | 24A / 25A |  | 13829 | 19600 | 23103 | 18744
D5FSHAH30XAK | D5CSRAH30AAK | 30,000/30,000 | 20.5 | 12 | 9.5 | YES | 3/8" x 3/4" | 164.04' | .32 Oz/Ft | 82.02' | 28A / 30A |  | 21495 | 20000 | 26498 | 9359
D5FSHAH36XAK | D5CSRAH36AAK | 36,000/36,000 | 19 | 8.7 | 8.5 | NO | 3/8" x 3/4" | 213.25' | .32 Oz/Ft | 98.43' | 33A / 35A |  | 22961 | 22000 | 26995 | 12885
4-Way Cassette 1:1 Deluxe Heat Pump Systems
D5FSCAH12XAK | D5CSHAH09AAK | 9,000/10,000 | 22.7 | 14 | 12.2 | YES | 1/4" x 3/8" | 82.02' | .16 Oz/Ft | 49.21' | 15A / 15A | 4200 | 7400 | 11000 | 11100 | 6483
D5FSCAH12XAK | D5CSHAH12AAK | 12,000/12,000 | 23.7 | 12.7 | 11.6 | YES | 1/4" x 3/8" | 82.02' | .16 Oz/Ft | 49.21' | 15A / 15A | 4300 | 7500 | 11500 | 11700 | 6558
D5FSCAH18XAK | D5CSHAH18AAK | 16,000/19,000 | 20 | 12.5 | 12.4 | YES | 1/4" x 1/2" | 98.42' | .16 Oz/Ft | 65.62' | 19A / 20A | 7800 | 14000 | 17000 | 14000 | 9879
D5FSCAH24XAK | D5CSHAH24AAK | 23,500/25,000 | 20.8 | 12 | 11.6 | YES | 3/8" x 5/8" | 164.04' | .32 Oz/Ft | 82.02' | 24.9A / 25A | 9500 | 17300 | 23800 | 21000 | 13293
D5FLCAH36XAK | D5CLHAH36AAK | 36,600/37,000 | 21.3 | 12 | 10.6 | YES | 3/8" x 3/4" | 246' | .32 Oz/Ft | 98.4' | 38A / 40A | 19200 | 30100 | 37000 | 34400 | 16842
D5FLCAH48XAK | D5CLHAH48AAK | 48,000 / 53,000 | 18.2 | 10 | 11 | NO | 3/8" x 3/4" | 246' | .32 Oz/Ft | 98.4' | 44A / 45A | 24000 | 38200 | 47500 | 38700 | 14068
4-Way Cassette 1:1 Quietcomfort Series Heat Pump Systems
D5FSCAH12XAK | D5CSRAH09AAK | 9,000/10,000 | 21.7 | 14.3 | 11.3 | YES | 1/4" x 3/8" | 82.02' | .16 Oz/Ft | 49.21' | 12A / 15A |  | 6100 | 8300 | 11700 | 7165
D5FSCAH12XAK | D5CSRAH12AAK | 12,000/12,000 | 21.2 | 12.5 | 10.4 | YES | 1/4" x 3/8" | 82.02' | .16 Oz/Ft | 49.21' | 12A / 15A |  | 6700 | 8400 | 11700 | 6735
D5FSCAH18XAK | D5CSRAH18AAK | 16,800/18,000 | 20.8 | 12.5 | 11.4 | YES | 1/4" x 1/2" | 98.42' | .16 Oz/Ft | 65.62' | 18A / 20A |  | 10600 | 12800 | 13400 | 4709
D5FSCAH24XAK | D5CSRAH24AAK | 24,000/25,000 | 22.1 | 12 | 10.5 | YES | 3/8" x 5/8" | 164.04' | .32 Oz/Ft | 82.02' | 24A / 25A |  | 12800 | 18500 | 21000 | 14388
D5FLCAH36XAK | D5CLRAH36AAK | 36,000/38,000 | 20 | 9.7 | 10.4 | NO | 3/8" x 3/4" | 246' | .32 Oz/Ft | 98.4' | 33A / 35A |  | 20800 | 26600 | 28200 | 16644
D5FLCAH48XAK | D5CLRAH48AAK | 48,000/50,000 | 19.1 | 9.5 | 9.9 | NO | 3/8" x 3/4" | 246' | .32 Oz/Ft | 98.4' | 39A / 40A |  | 32100 | 40500 | 40400 | 21475
Ceiling Cassette Grille for 9K, 12K & 18K BTU KSALG0103AAA (unbranded) ~ Ceiling Cassette Grille for 24K, 36K & 48K KSALG0203AAA (unbranded) [Required on all sizes and Sold Separately]
1-Way Cassette 1:1 Deluxe Heat Pump Systems
D5FSOAH06XAK | D5CSHAH06AAK | 6,500/7,400 | 22 | 15.2 | 12 | YES | 1/4" x 3/8" | 82.02' | .16 Oz/Ft | 49.21' | 12A / 15A | 4100 | 6400 | 8100 | 11200 | 6483
D5FSOAH12XAK | D5CSHAH09AAK | 9,000/10,900 | 24 | 14.7 | 12.2 | YES | 1/4" x 3/8" | 82.02' | .16 Oz/Ft | 49.21' | 15A / 15A | 5100 | 8600 | 10600 | 11200 | 6483
D5FSOAH12XAK | D5CSHAH12AAK | 12,000/12,500 | 23 | 13 | 10.2 | YES | 1/4" x 3/8" | 82.02' | .16 Oz/Ft | 49.21' | 15A / 15A | 5100 | 8600 | 11500 | 11900 | 6558
D5FSOAH18XAK | D5CSHAH18AAK | 16,700/20,000 | 20.7 | 12.5 | 12.2 | YES | 1/4" x 1/2" | 98.42' | .16 Oz/Ft | 65.62' | 19A / 20A | 9500 | 14500 | 17500 | 14500 | 10289
1-Way Cassette 1:1 Quietcomfort Heat Pump Systems
D5FSOAH12XAK | D5CSRAH09AAK | 9,000/11,000 | 22.2 | 14.4 | 11.8 | YES | 1/4" x 3/8" | 82.02' | .16 Oz/Ft | 49.21' | 12A / 15A |  | 6100 | 8000 | 10100 | 7165
D5FSOAH12XAK | D5CSRAH12AAK | 12,000/12,000 | 22.2 | 12.3 | 10.1 | YES | 1/4" x 3/8" | 82.02' | .16 Oz/Ft | 49.21' | 12A / 15A |  | 6800 | 8600 | 12400 | 7165
D5FSOAH18XAK | D5CSRAH18AAK | 18,000/18,000 | 22.3 | 12.5 | 12.2 | YES | 1/4" x 1/2" | 98.42' | .16 Oz/Ft | 65.62' | 18A / 20A |  | 10300 | 13100 | 14500 | 5118
One-Way Cassete units include grills ¦ 9k/12k IDU Capacity select via dip switch and must match ODU size
Floor Console 1:1 Deluxe Heat Pump Systems
D5FSFAH09XAK | D5CSHAH09AAK | 9,000/9,000 | 27.3 | 15.2 | 10.9 | YES | 1/4" x 3/8" | 82.02' | .16 Oz/Ft | 49.21' | 15A / 15A | 4700 | 8100 | 11300 | 11300 | 6483
D5FSFAH12XAK | D5CSHAH12AAK | 12,000/12,000 | 25 | 12.7 | 10.6 | YES | 1/4" x 3/8" | 82.02' | .16 Oz/Ft | 49.21' | 15A / 15A | 4800 | 8200 | 11300 | 11600 | 6558
D5FSFAH16XAK | D5CSHAH18AAK | 16,000/17,000 | 20.2 | 12.5 | 10.2 | YES | 1/4" x 1/2" | 98.42' | .16 Oz/Ft | 65.62' | 19A / 20A | 7600 | 13600 | 17500 | 13000 | 9107
Floor Console 1:1 Quietcomfort Series Heat Pump Systems
D5FSFAH09XAK | D5CSRAH09AAK | 9,000/9,000 | 26 | 16.3 | 13.9 | YES | 1/4" x 3/8" | 82.02' | .16 Oz/Ft | 49.21' | 12A / 15A |  | 6300 | 8600 | 10800 | 7165
D5FSFAH12XAK | D5CSRAH12AAK | 12,000/12,000 | 24.7 | 12.7 | 11 | YES | 1/4" x 3/8" | 82.02' | .16 Oz/Ft | 49.21' | 12A / 15A |  | 6300 | 8900 | 11500 | 6664
D5FSFAH16XAK | D5CSRAH18AAK | 16,000/17,000 | 23.9 | 12.5 | 13.5 | YES | 1/4" x 1/2" | 98.42' | .16 Oz/Ft | 65.62' | 18A / 20A |  | 10100 | 13100 | 13700 | 4811
Underceiling Console 1:1 Deluxe Heat Pump Systems
D5FCFAH18XAK | D5CSHAH18AAK | 18,000/18,000 | 22.4 | 12.5 | 10.4 | YES | 1/4" x 1/2" | 98.42' | .16 Oz/Ft | 65.62' | 19A / 20A | 9500 | 14500 | 17000 | 14500 | 10289
D5FCFAH24XAK | D5CSHAH24AAK | 24,000/24,500 | 21.2 | 12.2 | 11.1 | YES | 3/8" x 5/8" | 164.04' | .32 Oz/Ft | 82.02' | 24.9A / 25A | 10400 | 16500 | 24200 | 21200 | 13293
D5FCFAH36XAK | D5CLHAH36AAK | 36,000/38,000 | 20 | 10.2 | 10 | NO | 3/8" x 3/4" | 246' | .32 Oz/Ft | 98.4' | 38A / 40A | 26500 | 34500 | 39500 | 35200 | 18316
D5FCFAH48XAK | D5CLHAH48AAK | 48,000/50,000 | 19.9 | 9.5 | 10.2 | NO | 3/8" x 3/4" | 246' | .32 Oz/Ft | 98.4' | 44A / 45A | 22700 | 36000 | 47000 | 39700 | 23174
D5FCFAH58XAK | D5CLHAH58AAK | 54,000/60,000 | 19.5 | 9.6 | 9.5 | NO | 3/8" x 3/4" | 246' | .32 Oz/Ft | 98.4' | 44A / 45A | 29700 | 47700 | 54000 | 36700 | 10243
Underceiling Console 1:1 Quietcomfort Heat Pump Systems
D5FCFAH18XAK | D5CSRAH18AAK | 17,000/19,000 | 20.5 | 12.6 | 10.3 | YES | 1/4" x 1/2" | 98.42' | .16 Oz/Ft | 65.62' | 18A / 20A |  | 10500 | 12800 | 14800 | 5118
D5FCFAH24XAK | D5CSRAH24AAK | 22,000/26,000 | 20.5 | 12 | 12.1 | YES | 3/8" x 5/8" | 164.04' | .32 Oz/Ft | 82.02' | 24A / 25A |  | 12000 | 18600 | 21000 | 13293
D5FCFAH36XAK | D5CLRAH36AAK | 36,000/37,000 | 20.2 | 12 | 10.8 | YES | 3/8" x 3/4" | 246' | .32 Oz/Ft | 98.4' | 33A / 35A |  | 24100 | 26000 | 29500 | 17128
D5FCFAH48XAK | D5CLRAH48AAK | 48,000/50,000 | 18.7 | 9.4 | 10.1 | NO | 3/8" x 3/4" | 246' | .32 Oz/Ft | 98.4' | 39A / 40A |  | 34300 | 38500 | 41100 | 22444
D5FCFAH58XAK | D5CLRAH58AAK | 54,000/60,000 | 18.1 | 9 | 10.7 | NO | 3/8" x 3/4" | 246' | .32 Oz/Ft | 98.4' | 42A / 45A |  | 29500 | 35000 | 41200 | 18762
AHU 1:1 Deluxe Heat Pump Systems w/ Factory Installed 24V Interface
D5FSAAH18XBK | D5CSHAH18AAK | 18,000/19,500 | 18.2 | 12 | 10.1 | YES | 1/4" x 1/2" | 98.42' | .16 Oz/Ft | 65.62' | 19A / 20A | 9891 | 15484 | 18688 | 17391 | 12157
D5FSAAH24XBK | D5CSHAH24AAK | 23,000/26,000 | 18.8 | 12 | 10 | YES | 3/8" x 5/8" | 164.04' | .32 Oz/Ft | 82.02' | 24.9A / 25A | 12334 | 19483 | 24689 | 25819 | 16531
D5FSAAH30XBK | D5CSHAH33AAK | 33,000/35,000 | 16.7 | 11.7 | 10 | YES | 3/8" x 3/4" | 164.04' | .32 Oz/Ft | 82.02' | 38A / 40A | 21332 | 29944 | 35826 | 34216 | 15385
D5FLAAH36XAK | D5CLHCH36AAK | 36,000/38,000 | 17.3 | 11.7 | 9.5 | YES | 3/8" x 3/4" | 246' | .32 Oz/Ft | 98.4' | 44A / 45A | 24560 | 32267 | 39385 | 33526 | 14764
D5FLAAH48XAK | D5CLHCH48AAK | 48,000/50,000 | 17 | 10.1 | 10.2 | NO | 3/8" x 3/4" | 246' | .32 Oz/Ft | 98.4' | 12A / 15A | 22847 | 32097 | 41899 | 42510 | 27958
D5FLAAH60XAK | D5CLHCH58AAK | 54,000/59,000 | 15.4 | 10 | 9.2 | NO | 3/8" x 3/4" | 246' | .32 Oz/ft | 98.4' | 44A / 45A | 26637 | 41493 | 54678 | 37722 | 10562
AHU 1:1 Quietcomfort Heat Pump Systems w/ Factory Installed 24V Interface
D5FSAAH18XBK | D5CSRAH18AAK | 18,000/18,000 | 18.5 | 12.2 | 9.8 | YES | 1/4" x 1/2" | 98.42' | .16 Oz/ft | 65.62' | 18A / 20A |  | 10929 | 13689 | 15398 | 9595
D5FSAAH24XBK | D5CSRAH24AAK | 24,000/25,000 | 19.8 | 11.7 | 9 | YES | 3/8" x 5/8" | 164.04' | .32 Oz/ft | 82.02' | 24A / 25A |  | 15364 | 18920 | 23239 | 15108
D5FSAAH30XBK | D5CSRAH30AAK | 30,000/30,000 | 17 | 11 | 8.8 | NO | 3/8" x 3/4" | 164.04' | .32 Oz/ft | 82.02' | 28A / 30A |  | 12966 | 20820 | 27432 | 9475
D5FSAAH36XBK | D5CSRAH36AAK | 36,000/37,000 | 16 | 8.6 | 7.7 | NO | 3/8" x 3/4" | 213.25' | .32 Oz/ft | 98.43' | 33A / 35A |  | 18896 | 23536 | 27757 | 10062
D5FLAAH36XAK | D5CLRCH36AAK | 36,000/38,000 | 15.9 | 9 | 9.3 | NO | 3/8" x 3/4" | 246' | .32 Oz/ft | 98.4' | 33A / 35A |  | 21062 | 24802 | 28115 | 15282
D5FLAAH48XAK | D5CLRCH48AAK | 48,000/50,000 | 17.8 | 10 | 10 | NO | 3/8" x 3/4" | 246' | .32 Oz/ft | 98.4' | 39A / 40A |  | 32653 | 34918 | 43227 | 21724
D5FLAAH60XAK | D5CLRCH58AAK | 55,000/59,000 | 16 | 9.5 | 9.2 | NO | 3/8" x 3/4" | 246' | .32 Oz/ft | 98.4' | 42A / 45A |  | 29985 | 35954 | 42081 | 19276
Low Static Slim Ducted 1:1 Deluxe Heat Pump Systems
D5FSDAH06XAK | D5CSHAH06AAK | 6,500/8,000 | 21.5 | 14.5 | 13.8 | YES | 1/4" x 3/8" | 82.02' | .16 Oz/Ft | 49.21' | 12A / 15A | 4033 | 6302 | 7800 | 10448 | 7387
D5FSDAH12XAK | D5CSHAH09AAK | 9,000/10,000 | 21.5 | 13.5 | 12.5 | YES | 1/4" x 3/8" | 82.02' | .16 Oz/Ft | 49.21' | 15A / 15A | 6418 | 9704 | 11200 | 11147 | 6056
D5FSDAH12XAK | D5CSHAH12AAK | 12,000/12,500 | 20 | 12 | 10.2 | YES | 1/4" x 3/8" | 82.02' | .16 Oz/Ft | 49.21' | 15A / 15A | 6442 | 10256 | 11800 | 11430 | 6220
D5FSDAH18XAK | D5CSHAH18AAK | 17,000/19,000 | 18 | 12 | 10.8 | YES | 1/4" x 1/2" | 98.42' | .16 Oz/Ft | 65.62' | 19A / 20A | 10270 | 15917 | 18000 | 14525 | 10543
Low Static Slim Ducted 1:1 Quietcomfort Series Heat Pump Systems
D5FSDAH12XAK | D5CSRAH09AAK | 9,000/10,000 | 19.6 | 12.8 | 11 | YES | 1/4" x 3/8" | 82.02' | .16 Oz/Ft | 49.21' | 12A / 15A |  | 6899 | 8600 | 10577 | 7650
D5FSDAH12XAK | D5CSRAH12AAK | 11,500/12,000 | 19 | 11.7 | 10.3 | YES | 1/4" x 3/8" | 82.02' | .16 Oz/Ft | 49.21' | 12A / 15A |  | 6899 | 8800 | 10901 | 7820
D5FSDAH18XAK | D5CSRAH18AAK | 17,000/20,000 | 20 | 12.5 | 10.6 | YES | 1/4" x 1/2" | 98.42' | .16 Oz/Ft | 65.62' | 18A / 20A |  | 10297 | 14000 | 14310 | 7609
Low static slim ducted 9k/12k IDU Capacity select via dip switch and must match ODU size
High Static Slim Ducted 1:1 Deluxe Heat Pump Systems
D5FSDAH12XHK | D5CSHAH09AAK | 9,000/9,900 | 20.6 | 14 | 13.8 | YES | 1/4" x 3/8" | 82.02' | .16 Oz/Ft | 49.21' | 15A / 15A | 5418 | 8448 | 11900 | 11048 | 6060
D5FSDAH12XHK | D5CSHAH12AAK | 12,000/12,000 | 20.2 | 12 | 10.6 | YES | 1/4" x 3/8" | 82.02' | .16 Oz/Ft | 49.21' | 15A / 15A | 6688 | 10171 | 12000 | 11089 | 6537
D5FSDAH18XHK | D5CSHAH18AAK | 17,500/19,500 | 18.5 | 12.1 | 11.1 | YES | 1/4" x 1/2" | 98.42' | .16 Oz/Ft | 65.62' | 19A / 20A | 9195 | 15200 | 18000 | 15924 | 10325
D5FSDAH24XHK | D5CSHAH24AAK | 24,000/26,000 | 19.2 | 12 | 11.7 | YES | 3/8" x 5/8" | 164.04' | .32 Oz/Ft | 82.02' | 24.9A / 25A | 11539 | 19339 | 24000 | 20858 | 13979
D5FLDAH36XHK | D5CLHAH36AAK | 36,000/42,000 | 17.8 | 12 | 11.1 | YES | 3/8" x 3/4" | 246' | .32 Oz/Ft | 98.4' | 34A / 35A | 22946 | 31152 | 39385 | 33311 | 15545
D5FLDAH48XHK | D5CLHAH48AAK | 48,000/52,000 | 16.8 | 10.4 | 10.8 | NO | 3/8" x 3/4" | 246' | .32 Oz/Ft | 98.4' | 44A / 45A | 24826 | 38109 | 48560 | 41933 | 12003
D5FLDAH58XHK | D5CLHAH58AAK | 55,000/60,000 | 15.9 | 10.2 | 10.4 | NO | 3/8" x 3/4" | 246' | .32 Oz/Ft | 98.4' | 44A / 45A | 29858 | 45383 | 55902 | 39392 | 11014
9k/12k IDU Capacity select via dip switch and must match ODU size
High Static Slim Ducted 1:1 Quietcomfort Series Heat Pump Systems
D5FSDAH12XHK | D5CSRAH09AAK | 9,000/10,000 | 19.8 | 13 | 11.5 | YES | 1/4" x 3/8" | 82.02' | .16 Oz/Ft | 49.21' | 12A / 15A |  | 6554 | 8300 | 9690 | 7083
D5FSDAH12XHK | D5CSRAH12AAK | 12,000/12,000 | 19.5 | 12 | 10.5 | YES | 1/4" x 3/8" | 82.02' | .16 Oz/Ft | 49.21' | 12A / 15A |  | 7036 | 8900 | 10390 | 7776
D5FSDAH18XHK | D5CSRAH18AAK | 17,500/20,000 | 20 | 13.3 | 11.4 | YES | 1/4" x 1/2" | 98.42' | .16 Oz/Ft | 65.62' | 18A / 20A |  | 10663 | 14200 | 15303 | 5773
D5FSDAH24XHK | D5CSRAH24AAK | 24,000/25,000 | 19 | 12.5 | 11 | YES | 3/8" x 5/8" | 164.04' | .32 Oz/Ft | 82.02' | 24A / 25A |  | 15098 | 19000 | 21485 | 15668
D5FLDAH36XHK | D5CLRAH36AAK | 36,000/40,000 | 18.8 | 10.2 | 10.2 | NO | 3/8" x 3/4" | 246' | .32 Oz/Ft | 98.4' | 33A / 35A |  | 21421 | 26470 | 31407 | 16644
D5FLDAH48XHK | D5CLRAH48AAK | 48,000/50,000 | 17.2 | 10 | 9.8 | NO | 3/8" x 3/4" | 246' | .32 Oz/Ft | 98.4' | 39A / 40A |  | 32888 | 39357 | 42960 | 22369
D5FLDAH58XHK | D5CLRAH58AAK | 58,000/60,000 | 17 | 10 | 9.8 | NO | 3/8" x 3/4" | 246' | .32 Oz/Ft | 98.4' | 42A / 45A |  | 31868 | 39999 | 49604 | 22605
9k/12k IDU Capacity select via dip switch and must match ODU size
Performance Series High Wall 1:1 Heat Pump Systems
D5FEHAH09XCJ | D5CERAH09AAJ | 9,000/10,000 | 21.5 | 12.5 | 9.1 | YES | 1/4" x 3/8" | 82.02' | .16 Oz/Ft | 49.21' | 18A / 20A |  |  | 6797 | 8585 | 6128
D5FEHAH12XCJ | D5CERAH12AAJ | 12,000/12,000 | 21.4 | 10 | 8.7 | NO | 1/4" x 3/8" | 82.02' | .16 Oz/Ft | 49.21' | 19A / 20A |  |  | 6264 | 9325 | 4917
D5FEHAH09XCK | D5CERAH09AAK | 9,000/10,000 | 21.7 | 12.6 | 9.4 | YES | 1/4" x 3/8" | 82.02' | .16 Oz/Ft | 49.21' | 12A / 15A |  |  | 6459 | 8759 | 6483
D5FEHAH12XCK | D5CERAH12AAK | 12,000/12,000 | 21.4 | 10.8 | 9.2 | NO | 1/4" x 3/8" | 82.02' | .16 Oz/Ft | 49.21' | 13A / 15A |  |  | 7752 | 9427 | 4640
D5FEHAH18XCK | D5CERAH18AAK | 18,000/18,800 | 20.3 | 11.5 | 9.1 | NO | 1/4" x 1/2" | 98.42' | .16 Oz/Ft | 65.62' | 15A / 20A |  |  | 11493 | 14684 | 10539
D5FEHAH24XCK | D5CERAH24AAK | 24,000/24,000 | 18.5 | 9.7 | 9 | NO | 3/8" x 5/8" | 164.04' | .32 Oz/Ft | 82.02' | 19A / 20A |  |  | 16443 | 19646 | 14260
D5FEHAH30XCK | D5CERAH30AAK | 30,000/30,000 | 22.4 | 12 | 9 | YES | 3/8" x 5/8" | 164.04' | .32 Oz/Ft | 82.02' | 28A / 30A |  |  | 19812 | 27299 | 9137
D5FEHAH36XCK | D5CERAH36AAK | 36,000/36,000 | 19.5 | 9.4 | 9.1 | NO | 3/8" x 5/8" | 213.25' | .32 Oz/Ft | 98.4' | 33A / 35A |  |  | 25518 | 25709 | 9943
Performance Series High Wall 1:1 Air Conditioner Systems
D5FEHAA12XCJ | D5CERAA12AAJ | 11500 | 21.5 | 12 |  | YES | 1/4" x 3/8" | 82.02' | .16 Oz/Ft | 49.21' | 19A / 20A |  |  |  | 10338 | 5336
D5FEHAA09XCK | D5CERAA09AAK | 9000 | 20.5 | 12.5 |  | YES | 1/4" x 3/8" | 82.02' | .16 Oz/Ft | 49.21' | 9.9A / 15A |  |  |  | 8281 | 6445
D5FEHAA12XCK | D5CERAA12AAK | 11500 | 21 | 12 |  | YES | 1/4" x 3/8" | 82.02' | .16 Oz/Ft | 49.21' | 14A / 15A |  |  |  | 9922 | 6708
D5FEHAA18XCK | D5CERAA18AAK | 17500 | 22.2 | 11.7 |  | NO | 1/4" x 1/2" | 98.42' | .16 Oz/Ft | 65.62' | 16A / 20A |  |  |  | 14835 | 8080
D5FEHAA24XCK | D5CERAA24AAK | 22000 | 21.1 | 10.2 |  | NO | 3/8" x 5/8" | 164.04' | .32 Oz/Ft | 82.02' | 19A / 20A |  |  |  | 18764 | 14397
Accessories & Warranty Information
Use any 3rd party, 24V, 5-wire thermostat to control almost any ICP Ductless system by adding KSAIC0501230 or KSAIC0601230 24V Interface. Check the "Compatibility Charts" for updates regarding 24V interface compatibility.
Residential & Multi-Family Applications: 10 year limited warranty to original purchaser on compressor and parts when system is *registered within 90-days of installation. *Registration not required in CA and Quebec .
ICP No Hassle Warranty: Deluxe and QuietComfort Series ductless units qualify for No Hassle Warranty. See warranty certificate for full details and exclusions.
Commercial Applications: 7 year limited warranty to original purchaser on compressor and parts. See Warranty documents for full details
A Proud Member of the Carrier Family
©2025 Carrier. All rights reserved.
ENERGY STAR® is a registered trademark of the U.S. EPA.
DLS-050-CP-00 ¦ 02/2025

## Multi-Zone DLS
Multizone Quick Reference Guide - R-454B Ductless Systems
Outdoor Unit With Base Pan Heater | Max Zones | AHRI Rated Btu's Cooling @ 95F [35C] Heating @ 47F [6.3C] | SEER2 | EER2 | HSPF2 | Energy Star v6.1 Certified | Port Combinations |  | Max Line Set Length Per Zone | Max Total Line Set Length | Pre-Charge Length | Max. Lift | MCA/MOCP | Max Heating Capacity BTU's* At 70F [21.1C] Indoor DB @ Max CFM |  |  | Maximum Cooling BTU's* At 80F [26.7C] Indoor DB @ Max CFM
[7 empty] | Liquid | Suction | [5 empty] | @-22F [-30C] | @-4F [-20C] | @5F [-15C] | @110F [43C] | @122F [50C]
This sheet is not intended to replace the installation instructions. It is a reference guide only. Always read through the installation instructions.
Deluxe System Multi-Zone Heat Pump
D5CMHAH18CAK | 3 | 19000/20000 | 25 | 15 | 10.5 | YES | 3 @ 1/4" | 3 @ 3/8" | 98.4' | 196.9' | 73.8' | 49.21' | 17.5/20 | 10000 | 15000 | 19000 | 19600 | 10600
D5CMHAH24DAK | 4 | 24000/25000 | 24 | 13 | 10 | YES | 4 @ 1/4" | 3 @ 3/8" + 1 @ 1/2" | 114.8' | 262.5' | 98.4' | 49.21' | 30/35 | 14000 | 21000 | 25000 | 32000 | 19750
D5CMHAH30EAK | 5 | 30000/31000 | 24 | 13.2 | 10.7 | YES | 5 @ 1/4" | 3 @ 3/8" + 2 @ 1/2" | 114.8' | 262.5' | 123' | 49.21' | 37/40 | 22400 | 34400 | 36000 | 39000 | 19500
D5CMHAH36EAK | 5 | 36000/36000 | 23.1 | 13.1 | 10.7 | YES | 5 @ 1/4" | 3 @ 3/8" + 2 @ 1/2" | 114.8' | 262.5' | 123' | 49.21' | 37/40 | 22400 | 34400 | 36000 | 39000 | 19500
D5CMHAH48FAK | 6 | 47000/48500 | 23 | 12 | 11.3 | YES | 6 @ 1/4" | 4 @ 3/8" + 2 @ 1/2" | 114.8' | 262.5' | 147.6' | 49.21' | 37/40 | 24600 | 36000 | 47000 | 43000 | 27500
D5CMHAH55FAK | 6 | 52000/55000 | 22.3 | 12 | 10.5 | YES | 6 @ 1/4" | 4 @ 3/8" + 2 @ 1/2" | 114.8' | 262.5' | 147.6' | 49.21' | 39.5/40 | 26400 | 38500 | 47000 | 45000 | 30800
Quietcomfort Series Multi-Zone Heat Pump Systems
D5CMRAH18CAK | 3 | 18000/19000 | 25.2 | 14 | 9.8 | YES | 3 @ 1/4" | 3 @ 3/8" | 98.4' | 196.9' | 73.8' | 49.21' | 16/20 |  | 10000 | 13500 | 18800 | 10600
D5CMRAH24DAK | 4 | 24000/25000 | 25 | 13.5 | 9.5 | YES | 4 @ 1/4" | 3 @ 3/8" + 1 @ 1/2" | 114.8' | 262.5' | 98.4' | 49.21' | 23/25 |  | 11000 | 18000 | 26000 | 14850
D5CMRAH30EAK | 5 | 30000/31000 | 25 | 13 | 10 | YES | 5 @ 1/4" | 3 @ 3/8" + 2 @ 1/2" | 114.8' | 262.5' | 123' | 49.21' | 30.5/35 |  | 19300 | 26000 | 30600 | 23500
D5CMRAH36EAK | 5 | 35400/37000 | 24 | 12 | 9.5 | YES | 5 @ 1/4" | 3 @ 3/8" + 2 @ 1/2" | 114.8' | 262.5' | 123' | 49.21' | 30.5/35 |  | 19300 | 26000 | 30600 | 23500
D5CMRAH48FAK | 6 | 46000/47500 | 24 | 12.5 | 10.4 | YES | 6 @ 1/4" | 4 @ 3/8" + 2 @ 1/2" | 114.8' | 262.5' | 147.6' | 49.21' | 34/40 |  | 32200 | 36000 | 42000 | 25700
D5CMRAH55FAK | 6 | 60000/60000 | 22 | 10 | 9.6 | NO | 6 @ 1/4" | 4 @ 3/8" + 2 @ 1/2" | 114.8' | 262.5' | 147.6' | 49.21' | 36/40 |  | 33000 | 39000 | 46000 | 25700
*All ratings, heating/cooling capacities, and Energy Star certification based on non-ducted indoor units. Check most recent product data documents for other system applications.
Indoor Unit Types, Models, and Approved Btu/hr Combinations
Installation Notes
Port adaptors included with the outdoor units and no branch boxes required.
10' minimum line length require per zone.
Minimum 2 zones must be connected.
Up to 2 AHUs can be used for the following combinations only: 18+18, 18+24, 18+30, 18+36, 24+24, 24+30, 24+36. In the case that 2 AHU units are selected, no other units may be connected to the outdoor unit, regardless of remaining ports or capacity availability.
When a 30k or 36k AHU is utilized with a Multi-Zone ODU, 500 grams (17.6 Oz) of additional refrigerant should be added to the system.
One-Way Cassette sizing is determined by capacity rotary swith on IDU.
Wi-Fi Kits and Wire Remote Controllers compatible with single or multi-zone as per IDU compatibility.
A Proud Member of the Carrier Family
©2025 Carrier. All rights reserved.
ENERGY STAR® is a registered trademark of the U.S. EPA.
DLS-050-CP-00 ¦ 02/2025

## Multi-Zone Combination Chart
Multizone Quick Reference Guide - R-454B Systems
Combinations valid for D5CM(H/R)AH units.
| Two Zones |  | Three Zones |  |  | Four Zones |  |  |  |  | Five Zones |  |  |  |  | Six Zones
D5CMRAH18CAK | 6+6 | 6+18 | 6+6+6
| 6+9 | 9+9 | 6+6+9
| 6+12 | 9+12 | 6+9+9
12+12
D5CMHAH18CAK D5CMRAH24DAK | 6+6 | 9+12 | 6+6+6 | 6+9+18 | 12+12+12 | 6+6+6+6 | 9+9+9+9
| 6+9 | 9+18 | 6+6+9 | 6+12+12 |  | 6+6+6+9
| 6+12 | 9+24 | 6+6+12 | 6+12+18 |  | 6+6+6+12
| 6+18 | 12+12 | 6+6+18 | 9+9+9 |  | 6+6+9+9
| 6+24 | 12+18 | 6+6+24 | 9+9+12 |  | 6+6+9+12
| 9+9 | 12+24 | 6+9+9 | 9+9+18 |  | 6+9+9+9
| 18+18 |  | 6+9+12 | 9+12+12 |  | 6+9+9+12
37MGRAQ24DA3 | 6+6 | 9+12 | 6+6+6 | 6+9+18 | 12+12+12 | 6+6+6+6 | 9+9+9+9
| 6+9 | 9+18 | 6+6+9 | 6+12+12 |  | 6+6+6+9
| 6+12 | 9+24 | 6+6+12 | 6+12+18 |  | 6+6+6+12
| 6+18 | 12+12 | 6+6+18 | 9+9+9 |  | 6+6+9+9
| 6+24 | 12+18 | 6+6+24 | 9+9+12 |  | 6+6+9+12
| 9+9 | 12+24 | 6+9+9 | 9+9+18 |  | 6+9+9+9
| 18+18 |  | 6+9+12 | 9+12+12 |  | 6+9+9+12
D5CMHAH24DAK | 6+18 | 9+24 | 6+6+6 | 6+12+12 | 9+12+12 | 6+6+6+6 | 6+6+12+12 | 6+9+12+18 | 12+12+12+12
| 6+24 | 12+12 | 6+6+9 | 6+12+18 | 9+12+18 | 6+6+6+9 | 6+6+12+18 | 6+12+12+12
| 9+9 | 12+18 | 6+6+12 | 6+12+24 | 9+12+24 | 6+6+6+12 | 6+6+12+24 | 6+12+12+18
| 9+12 | 12+24 | 6+6+18 | 6+18+18 | 9+18+18 | 6+6+6+18 | 6+6+18+18 | 9+9+9+9
| 9+18 | 18+18 | 6+6+24 | 6+18+24 | 12+12+12 | 6+6+6+24 | 6+9+9+9 | 9+9+9+12
|  |  | 6+9+9 | 9+9+9 | 12+12+18 | 6+6+9+9 | 6+9+9+12 | 9+9+9+18
|  |  | 6+9+12 | 9+9+12 | 12+12+24 | 6+6+9+12 | 6+9+9+18 | 9+9+12+12
|  |  | 6+9+18 | 9+9+18 | 12+18+18 | 6+6+9+18 | 6+9+9+24 | 9+9+12+18
|  |  | 6+9+24 | 9+9+24 |  | 6+6+9+24 | 6+9+12+12 | 9+12+12+12
D5CMRAH30EAK D5CMRAH36EAK | 6+18 | 9+24 | 6+6+6 | 6+12+12 | 9+12+18 | 6+6+6+6 | 6+6+12+12 | 6+9+12+18 | 12+12+12+12 |  | 6+6+6+6+6 | 6+6+9+9+18
| 6+24 | 12+12 | 6+6+9 | 6+12+18 | 9+12+24 | 6+6+6+9 | 6+6+12+18 | 6+12+12+12 |  |  | 6+6+6+6+9 | 6+9+9+9+9
| 9+9 | 12+18 | 6+6+12 | 6+12+24 | 9+18+18 | 6+6+6+12 | 6+6+12+24 | 6+12+12+18 |  |  | 6+6+6+6+12 | 6+9+9+9+12
| 9+12 | 12+24 | 6+6+18 | 6+18+18 | 12+12+12 | 6+6+6+18 | 6+6+18+18 | 9+9+9+9 |  |  | 6+6+6+6+18 | 6+9+9+9+18
| 9+18 | 18+18 | 6+6+24 | 9+9+9 | 12+12+18 | 6+6+6+24 | 6+9+9+9 | 9+9+9+12 |  |  | 6+6+6+9+9 | 9+9+9+9+9
|  |  | 6+9+9 | 9+9+12 | 12+12+24 | 6+6+9+9 | 6+9+9+12 | 9+9+9+18 |  |  | 6+6+6+9+12 | 9+9+9+9+12
|  |  | 6+9+12 | 9+9+18 | 12+18+18 | 6+6+9+12 | 6+9+9+18 | 9+9+12+12 |  |  | 6+6+6+9+18
|  |  | 6+9+18 | 9+9+24 |  | 6+6+9+18 | 6+9+9+24 | 9+9+12+18 |  |  | 6+6+9+9+9
|  |  | 6+9+24 | 9+12+12 |  | 6+6+9+24 | 6+9+12+12 | 9+12+12+12 |  |  | 6+6+9+9+12
D5CMHAH30EAK D5CMHAH36EAK | 6+24 | 12+18 | 6+6+12 | 6+12+18 | 9+12+18 | 6+6+6+6 | 6+6+12+24 | 6+9+18+24 | 9+9+12+12 | 12+12+12+18 | 6+6+6+6+6 | 6+6+9+9+18
| 6+30 | 12+24 | 6+6+18 | 6+12+24 | 9+12+24 | 6+6+6+9 | 6+6+18+18 | 6+12+12+12 | 9+9+12+18 | 12+12+12+24 | 6+6+6+6+9 | 6+6+9+12+12
| 6+36 | 12+30 | 6+6+24 | 6+12+30 | 9+18+18 | 6+6+6+12 | 6+6+18+24 | 6+12+12+18 | 9+9+12+24 | 12+12+18+18 | 6+6+6+6+12 | 6+6+12+12+12
| 9+18 | 12+36 | 6+6+30 | 6+18+18 | 9+18+24 | 6+6+6+18 | 6+9+9+9 | 6+12+12+24 | 9+9+18+18 |  | 6+6+6+6+18 | 6+9+9+9+9
| 9+24 | 18+18 | 6+6+36 | 6+18+24 | 12+12+12 | 6+6+6+24 | 6+9+9+12 | 6+12+18+18 | 9+9+18+24 |  | 6+6+6+9+9 | 6+9+9+9+12
| 9+30 | 18+24 | 6+9+9 | 9+9+9 | 12+12+18 | 6+6+9+9 | 6+9+9+18 | 6+12+18+24 | 9+12+12+12 |  | 6+6+6+9+12 | 6+9+9+12+12
| 9+36 | 18+30 | 6+9+12 | 9+9+12 | 12+12+24 | 6+6+9+12 | 6+9+9+24 | 6+18+18+18 | 9+12+12+18 |  | 6+6+6+9+18 | 9+9+9+9+9
| 12+12 | 24+24 | 6+9+18 | 9+9+18 | 12+18+18 | 6+6+9+18 | 6+9+12+12 | 9+9+9+9 | 9+12+12+24 |  | 6+6+6+12+12 | 9+9+9+9+12
|  |  | 6+9+24 | 9+9+24 | 12+18+24 | 6+6+9+24 | 6+9+12+18 | 9+9+9+12 | 9+12+18+18 |  | 6+6+6+12+18
|  |  | 6+9+30 | 9+9+30 | 18+18+18 | 6+6+12+12 | 6+9+12+24 | 9+9+9+18 | 9+18+18+18 |  | 6+6+9+9+9
|  |  | 6+12+12 | 9+12+12 |  | 6+6+12+18 | 6+9+18+18 | 9+9+9+24 | 12+12+12+12 |  | 6+6+9+9+12
D5CMRAH48FAK | 6+24 | 12+24 | 6+6+18 | 6+18+24 | 9+18+18 | 6+6+6+6 | 6+9+9+12 | 9+9+9+12 | 12+12+12+12 |  | 6+6+6+6+6 | 6+6+9+9+9 | 6+9+9+9+12 | 9+9+9+9+12 |  | 6+6+6+6+6+6 | 6+6+6+12+12+12 | 6+9+9+12+12+12
| 6+30 | 12+30 | 6+6+24 | 6+18+30 | 9+18+24 | 6+6+6+9 | 6+9+9+18 | 9+9+9+18 | 12+12+12+18 |  | 6+6+6+6+9 | 6+6+9+9+12 | 6+9+9+9+18 | 9+9+9+9+18 |  | 6+6+6+6+6+9 | 6+6+6+12+12+18 | 9+9+9+9+9+9
| 6+36 | 12+36 | 6+6+30 | 6+18+36 | 9+18+30 | 6+6+6+18 | 6+9+9+24 | 9+9+9+24 | 12+12+12+24 |  | 6+6+6+6+12 | 6+6+9+9+18 | 6+9+9+9+24 | 9+9+9+9+24 |  | 6+6+6+6+6+12 | 6+6+9+9+9+9 | 9+9+9+9+9+12
| 9+18 | 18+18 | 6+6+36 | 9+9+9 | 9+18+36 | 6+6+6+24 | 6+9+12+12 | 9+9+12+12 | 12+12+18+18 |  | 6+6+6+6+18 | 6+6+9+9+24 | 6+9+9+12+12 | 9+9+9+12+12 |  | 6+6+6+6+6+18 | 6+6+9+9+9+12 | 9+9+9+9+9+18
| 9+24 | 18+24 | 6+9+12 | 9+9+12 | 12+12+12 | 6+6+9+9 | 6+9+12+18 | 9+9+12+18 |  |  | 6+6+6+6+24 | 6+6+9+12+12 | 6+9+9+12+18 | 9+9+9+12+18 |  | 6+6+6+6+9+9 | 6+6+9+9+9+18 | 9+9+9+9+12+12
| 9+30 | 18+30 | 6+9+18 | 9+9+18 | 12+12+18 | 6+6+9+12 | 6+9+12+24 | 9+9+12+24 |  |  | 6+6+6+9+9 | 6+6+9+12+18 | 6+9+9+12+24 | 9+9+9+12+24 |  | 6+6+6+6+9+12 | 6+6+9+9+12+12 | 9+9+9+12+12+12
| 9+36 | 18+36 | 6+9+24 | 9+9+24 | 12+12+24 | 6+6+9+18 | 6+9+18+18 | 9+9+18+18 |  |  | 6+6+6+9+12 | 6+6+9+12+24 | 6+9+9+18+18 | 9+9+9+18+18 |  | 6+6+6+6+9+18 | 6+6+9+9+12+18
| 12+12 | 24+24 | 6+9+30 | 9+9+30 | 12+12+30 | 6+6+9+24 | 6+9+18+24 | 9+9+18+24 |  |  | 6+6+6+9+18 | 6+6+9+18+18 | 6+9+12+12+12 | 9+9+12+12+12 |  | 6+6+6+6+12+12 | 6+6+9+12+12+12
| 12+18 | 24+30 | 6+9+36 | 9+9+36 | 12+12+36 | 6+6+12+12 | 6+12+12+12 | 9+12+12+12 |  |  | 6+6+6+9+24 | 6+6+9+18+24 | 6+9+12+12+18 | 9+9+12+12+18 |  | 6+6+6+6+12+18 | 6+6+9+12+12+18
| 24+36 |  | 6+12+18 | 9+12+12 | 12+18+18 | 6+6+12+18 | 6+12+12+18 | 9+12+12+18 |  |  | 6+6+6+12+12 | 6+6+12+12+12 | 6+9+12+12+24 | 9+12+12+12+12 |  | 6+6+6+9+9+9 | 6+9+9+9+9+9
|  |  | 6+12+24 | 9+12+18 | 12+18+24 | 6+6+12+24 | 6+12+12+24 | 9+12+12+24 |  |  | 6+6+6+12+18 | 6+6+12+12+18 | 6+9+12+18+18 | 9+12+12+12+18 |  | 6+6+6+9+9+12 | 6+9+9+9+9+12
|  |  | 6+12+30 | 9+12+24 | 12+18+30 | 6+6+18+18 | 6+12+18+18 | 9+12+18+18 |  |  | 6+6+6+12+24 | 6+6+12+12+24 | 6+12+12+12+12 | 12+12+12+12+12 |  | 6+6+6+9+9+18 | 6+9+9+9+9+18
|  |  | 6+12+36 | 9+12+30 | 18+18+18 | 6+6+18+24 | 6+12+18+24 | 9+12+18+24 |  |  | 6+6+6+18+18 | 6+6+12+18+18 | 6+12+12+12+18 |  |  | 6+6+6+9+12+12 | 6+9+9+9+12+12
|  |  | 6+18+18 | 9+12+36 |  | 6+9+9+9 | 9+9+9+9 | 9+18+18+18 |  |  | 6+6+6+18+24 | 6+9+9+9+9 | 9+9+9+9+9 |  |  | 6+6+6+9+12+18 | 6+9+9+9+12+18
D5CMHAH48FAK | 6+24 | 12+24 | 6+6+18 | 6+18+18 | 9+18+18 | 6+6+6+6 | 6+9+9+12 | 9+9+9+9 | 12+12+12+12 |  | 6+6+6+6+6 | 6+6+9+9+12 | 6+9+9+9+9 | 6+12+12+12+12 | 9+9+12+12+18 | 6+6+6+6+6+6 | 6+6+6+9+9+24 | 6+6+9+12+12+18 | 6+9+12+12+12+12 | 9+12+12+12+12+12
| 6+30 | 12+30 | 6+6+24 | 6+18+24 | 9+18+24 | 6+6+6+9 | 6+9+9+18 | 9+9+9+12 | 12+12+12+18 |  | 6+6+6+6+9 | 6+6+9+9+18 | 6+9+9+9+12 | 6+12+12+12+18 | 9+9+12+12+24 | 6+6+6+6+6+9 | 6+6+6+9+12+12 | 6+6+9+12+12+24 | 6+9+12+12+12+18 | 12+12+12+12+12+12
| 6+36 | 12+36 | 6+6+30 | 6+18+30 | 9+18+30 | 6+6+6+12 | 6+9+9+24 | 9+9+9+18 | 12+12+12+24 |  | 6+6+6+6+12 | 6+6+9+9+24 | 6+9+9+9+18 | 6+12+12+12+24 | 9+9+12+18+18 | 6+6+6+6+6+12 | 6+6+6+9+12+18 | 6+6+12+12+12+12 | 6+12+12+12+12+12
| 9+18 | 18+18 | 6+6+36 | 6+18+36 | 9+18+36 | 6+6+6+18 | 6+9+12+12 | 9+9+9+24 | 12+12+18+18 |  | 6+6+6+6+18 | 6+6+9+12+12 | 6+9+9+9+24 | 6+12+12+18+18 | 9+9+12+18+24 | 6+6+6+6+6+18 | 6+6+6+9+12+24 | 6+6+12+12+12+18 | 6+12+12+12+12+18
| 9+24 | 18+24 | 6+9+9 | 9+9+9 | 12+12+12 | 6+6+6+24 | 6+9+12+18 | 9+9+12+12 | 12+12+18+24 |  | 6+6+6+6+24 | 6+6+9+12+18 | 6+9+9+12+12 | 6+12+18+18+18 | 9+9+18+18+18 | 6+6+6+6+6+24 | 6+6+6+12+12+12 | 6+6+12+12+12+24 | 9+9+9+9+9+9
| 9+30 | 18+30 | 6+9+12 | 9+9+12 | 12+12+18 | 6+6+9+9 | 6+9+12+24 | 9+9+12+18 | 12+18+18+18 |  | 6+6+6+9+9 | 6+6+9+12+24 | 6+9+9+12+18 | 9+9+9+9+9 | 9+12+12+12+12 | 6+6+6+6+9+9 | 6+6+6+12+12+18 | 6+9+9+9+9+9 | 9+9+9+9+9+12
| 9+36 | 18+36 | 6+9+18 | 9+9+18 | 12+12+24 | 6+6+9+12 | 6+9+18+18 | 9+9+12+24 |  |  | 6+6+6+9+12 | 6+6+9+18+18 | 6+9+9+12+24 | 9+9+9+9+12 | 9+12+12+12+18 | 6+6+6+6+9+12 | 6+6+6+12+12+24 | 6+9+9+9+9+12 | 9+9+9+9+9+18
| 12+12 | 24+24 | 6+9+24 | 9+9+24 | 12+12+30 | 6+6+9+18 | 6+9+18+24 | 9+9+18+18 |  |  | 6+6+6+9+18 | 6+6+9+18+24 | 6+9+9+18+18 | 9+9+9+9+18 | 9+12+12+12+24 | 6+6+6+6+9+18 | 6+6+9+9+9+9 | 6+9+9+9+9+18 | 9+9+9+9+9+24
| 12+18 | 24+30 | 6+9+30 | 9+9+30 | 12+12+36 | 6+6+9+24 | 6+12+12+12 | 9+9+18+24 |  |  | 6+6+6+9+24 | 6+6+12+12+12 | 6+9+9+18+24 | 9+9+9+9+24 | 9+12+12+18+18 | 6+6+6+6+9+24 | 6+6+9+9+9+12 | 6+9+9+9+9+24 | 9+9+9+9+12+12
| 24+36 |  | 6+9+36 | 9+9+36 | 12+18+18 | 6+6+12+12 | 6+12+12+18 | 9+12+12+12 |  |  | 6+6+6+12+12 | 6+6+12+12+18 | 6+9+12+12+12 | 9+9+9+12+12 | 12+12+12+12+12 | 6+6+6+6+12+12 | 6+6+9+9+9+18 | 6+9+9+9+12+12 | 9+9+9+9+12+18
|  |  | 6+12+12 | 9+12+12 | 12+18+24 | 6+6+12+18 | 6+12+12+24 | 9+12+12+18 |  |  | 6+6+6+12+18 | 6+6+12+12+24 | 6+9+12+12+18 | 9+9+9+12+18 | 12+12+12+12+18 | 6+6+6+6+12+18 | 6+6+9+9+9+24 | 6+9+9+9+12+18 | 9+9+9+9+12+24
|  |  | 6+12+18 | 9+12+18 | 12+18+30 | 6+6+12+24 | 6+12+18+18 | 9+12+12+24 |  |  | 6+6+6+12+24 | 6+6+12+18+18 | 6+9+12+12+24 | 9+9+9+12+24 | 12+12+12+12+24 | 6+6+6+6+12+24 | 6+6+9+9+12+12 | 6+9+9+9+12+24 | 9+9+9+12+12+12
|  |  | 6+12+24 | 9+12+24 | 12+18+36 | 6+6+18+18 | 6+12+18+24 | 9+12+18+18 |  |  | 6+6+6+18+18 | 6+6+12+18+24 | 6+9+12+18+18 | 9+9+9+18+18 | 12+12+12+18+18 | 6+6+6+9+9+9 | 6+6+9+9+12+18 | 6+9+9+12+12+12 | 9+9+9+12+12+18
|  |  | 6+12+30 | 9+12+30 | 18+18+18 | 6+6+18+24 | 6+18+18+18 | 9+12+18+24 |  |  | 6+6+6+18+24 | 6+6+18+18+18 | 6+9+12+18+24 | 9+9+9+18+24 |  | 6+6+6+9+9+12 | 6+6+9+9+12+24 | 6+9+9+12+12+18 | 9+9+12+12+12+12
|  |  | 6+12+36 | 9+12+36 |  | 6+9+9+9 | 6+18+18+24 | 9+18+18+18 |  |  | 6+6+9+9+9 | 6+6+18+18+24 | 6+9+18+18+18 | 9+9+12+12+12 |  | 6+6+6+9+9+18 | 6+6+9+12+12+12 | 6+9+9+12+12+24 | 9+9+12+12+12+18
D5CMRAH55FAK | 6+24 | 12+24 | 6+6+18 | 6+18+18 | 9+18+18 | 6+6+6+6 | 6+9+9+12 | 9+9+9+9 | 12+12+12+12 |  | 6+6+6+6+6 | 6+6+9+9+12 | 6+9+9+9+9 | 6+12+12+12+12 | 9+9+12+12+18 | 6+6+6+6+6+6 | 6+6+6+9+9+24 | 6+6+9+12+12+18 | 6+9+9+12+12+24 | 9+9+12+12+12+18
| 6+30 | 12+30 | 6+6+24 | 6+18+24 | 9+18+24 | 6+6+6+9 | 6+9+9+18 | 9+9+9+12 | 12+12+12+18 |  | 6+6+6+6+9 | 6+6+9+9+18 | 6+9+9+9+12 | 6+12+12+12+18 | 9+9+12+12+24 | 6+6+6+6+6+9 | 6+6+6+9+12+12 | 6+6+9+12+12+24 | 6+9+12+12+12+12 | 9+12+12+12+12+12
| 6+36 | 12+36 | 6+6+30 | 6+18+30 | 9+18+30 | 6+6+6+12 | 6+9+9+24 | 9+9+9+18 | 12+12+12+24 |  | 6+6+6+6+12 | 6+6+9+9+24 | 6+9+9+9+18 | 6+12+12+12+24 | 9+9+12+18+18 | 6+6+6+6+6+12 | 6+6+6+9+12+18 | 6+6+12+12+12+12 | 6+9+12+12+12+18 | 12+12+12+12+12+12
| 9+18 | 18+18 | 6+6+36 | 6+18+36 | 9+18+36 | 6+6+6+18 | 6+9+12+12 | 9+9+9+24 | 12+12+18+18 |  | 6+6+6+6+18 | 6+6+9+12+12 | 6+9+9+9+24 | 6+12+12+18+18 | 9+9+12+18+24 | 6+6+6+6+6+18 | 6+6+6+9+12+24 | 6+6+12+12+12+18 | 6+12+12+12+12+12
| 9+24 | 18+24 | 6+9+9 | 9+9+9 | 12+12+12 | 6+6+6+24 | 6+9+12+18 | 9+9+12+12 | 12+12+18+24 |  | 6+6+6+6+24 | 6+6+9+12+18 | 6+9+9+12+12 | 6+12+18+18+18 | 9+9+18+18+18 | 6+6+6+6+6+24 | 6+6+6+12+12+12 | 6+6+12+12+12+24 | 6+12+12+12+12+18
| 9+30 | 18+30 | 6+9+12 | 9+9+12 | 12+12+18 | 6+6+9+9 | 6+9+12+24 | 9+9+12+18 | 12+18+18+18 |  | 6+6+6+9+9 | 6+6+9+12+24 | 6+9+9+12+18 | 9+9+9+9+9 | 9+12+12+12+12 | 6+6+6+6+9+9 | 6+6+6+12+12+18 | 6+9+9+9+9+9 | 9+9+9+9+9+9
| 9+36 | 18+36 | 6+9+18 | 9+9+18 | 12+12+24 | 6+6+9+12 | 6+9+18+18 | 9+9+12+24 |  |  | 6+6+6+9+12 | 6+6+9+18+18 | 6+9+9+12+24 | 9+9+9+9+12 | 9+12+12+12+18 | 6+6+6+6+9+12 | 6+6+6+12+12+24 | 6+9+9+9+9+12 | 9+9+9+9+9+12
| 12+12 | 24+24 | 6+9+24 | 9+9+24 | 12+12+30 | 6+6+9+18 | 6+9+18+24 | 9+9+18+18 |  |  | 6+6+6+9+18 | 6+6+9+18+24 | 6+9+9+18+18 | 9+9+9+9+18 | 9+12+12+12+24 | 6+6+6+6+9+18 | 6+6+9+9+9+9 | 6+9+9+9+9+18 | 9+9+9+9+9+18
| 12+18 | 24+30 | 6+9+30 | 9+9+30 | 12+12+36 | 6+6+9+24 | 6+12+12+12 | 9+9+18+24 |  |  | 6+6+6+9+24 | 6+6+12+12+12 | 6+9+9+18+24 | 9+9+9+9+24 | 9+12+12+18+18 | 6+6+6+6+9+24 | 6+6+9+9+9+12 | 6+9+9+9+9+24 | 9+9+9+9+9+24
| 24+36 |  | 6+9+36 | 9+9+36 | 12+18+18 | 6+6+12+12 | 6+12+12+18 | 9+12+12+12 |  |  | 6+6+6+12+12 | 6+6+12+12+18 | 6+9+12+12+12 | 9+9+9+12+12 | 12+12+12+12+12 | 6+6+6+6+12+12 | 6+6+9+9+9+18 | 6+9+9+9+12+12 | 9+9+9+9+12+12
|  |  | 6+12+12 | 9+12+12 | 12+18+24 | 6+6+12+18 | 6+12+12+24 | 9+12+12+18 |  |  | 6+6+6+12+18 | 6+6+12+12+24 | 6+9+12+12+18 | 9+9+9+12+18 | 12+12+12+12+18 | 6+6+6+6+12+18 | 6+6+9+9+9+24 | 6+9+9+9+12+18 | 9+9+9+9+12+18
|  |  | 6+12+18 | 9+12+18 | 12+18+30 | 6+6+12+24 | 6+12+18+18 | 9+12+12+24 |  |  | 6+6+6+12+24 | 6+6+12+18+18 | 6+9+12+12+24 | 9+9+9+12+24 | 12+12+12+12+24 | 6+6+6+6+12+24 | 6+6+9+9+12+12 | 6+9+9+9+12+24 | 9+9+9+9+12+24
|  |  | 6+12+24 | 9+12+24 | 12+18+36 | 6+6+18+18 | 6+12+18+24 | 9+12+18+18 |  |  | 6+6+6+18+18 | 6+6+12+18+24 | 6+9+12+18+18 | 9+9+9+18+18 | 12+12+12+18+18 | 6+6+6+9+9+9 | 6+6+9+9+12+18 | 6+9+9+9+18+18 | 9+9+9+12+12+12
|  |  | 6+12+30 | 9+12+30 | 18+18+18 | 6+6+18+24 | 6+18+18+18 | 9+12+18+24 |  |  | 6+6+6+18+24 | 6+6+18+18+18 | 6+9+12+18+24 | 9+9+9+18+24 |  | 6+6+6+9+9+12 | 6+6+9+9+12+24 | 6+9+9+12+12+12 | 9+9+9+12+12+18
|  |  | 6+12+36 | 9+12+36 |  | 6+9+9+9 | 6+18+18+24 | 9+18+18+18 |  |  | 6+6+9+9+9 | 6+6+18+18+24 | 6+9+18+18+18 | 9+9+12+12+12 |  | 6+6+6+9+9+18 | 6+6+9+12+12+12 | 6+9+9+12+12+18 | 9+9+12+12+12+12
D5CMHAH55FAK | 6+24 | 12+24 | 6+6+18 | 6+18+18 | 9+18+18 | 6+6+6+6 | 6+9+9+12 | 9+9+9+9 | 12+12+12+12 |  | 6+6+6+6+6 | 6+6+9+9+12 | 6+9+9+9+9 | 6+12+12+12+12 | 9+9+12+12+18 | 6+6+6+6+6+6 | 6+6+6+9+9+24 | 6+6+9+12+12+18 | 6+9+12+12+12+12 | 9+12+12+12+12+12
| 6+30 | 12+30 | 6+6+24 | 6+18+24 | 9+18+24 | 6+6+6+9 | 6+9+9+18 | 9+9+9+12 | 12+12+12+18 |  | 6+6+6+6+9 | 6+6+9+9+18 | 6+9+9+9+12 | 6+12+12+12+18 | 9+9+12+12+24 | 6+6+6+6+6+9 | 6+6+6+9+12+12 | 6+6+9+12+12+24 | 6+9+12+12+12+18 | 12+12+12+12+12+12
| 6+36 | 12+36 | 6+6+30 | 6+18+30 | 9+18+30 | 6+6+6+12 | 6+9+9+24 | 9+9+9+18 | 12+12+12+24 |  | 6+6+6+6+12 | 6+6+9+9+24 | 6+9+9+9+18 | 6+12+12+12+24 | 9+9+12+18+18 | 6+6+6+6+6+12 | 6+6+6+9+12+18 | 6+6+12+12+12+12 | 6+12+12+12+12+12
| 9+18 | 18+18 | 6+6+36 | 6+18+36 | 9+18+36 | 6+6+6+18 | 6+9+12+12 | 9+9+9+24 | 12+12+18+18 |  | 6+6+6+6+18 | 6+6+9+12+12 | 6+9+9+9+24 | 6+12+12+18+18 | 9+9+12+18+24 | 6+6+6+6+6+18 | 6+6+6+9+12+24 | 6+6+12+12+12+18 | 6+12+12+12+12+18
| 9+24 | 18+24 | 6+9+9 | 9+9+9 | 12+12+12 | 6+6+6+24 | 6+9+12+18 | 9+9+12+12 | 12+12+18+24 |  | 6+6+6+6+24 | 6+6+9+12+18 | 6+9+9+12+12 | 6+12+18+18+18 | 9+9+18+18+18 | 6+6+6+6+6+24 | 6+6+6+12+12+12 | 6+6+12+12+12+24 | 9+9+9+9+9+9
| 9+30 | 18+30 | 6+9+12 | 9+9+12 | 12+12+18 | 6+6+9+9 | 6+9+12+24 | 9+9+12+18 | 12+18+18+18 |  | 6+6+6+9+9 | 6+6+9+12+24 | 6+9+9+12+18 | 9+9+9+9+9 | 9+12+12+12+12 | 6+6+6+6+9+9 | 6+6+6+12+12+18 | 6+9+9+9+9+9 | 9+9+9+9+9+12
| 9+36 | 18+36 | 6+9+18 | 9+9+18 | 12+12+24 | 6+6+9+12 | 6+9+18+18 | 9+9+12+24 |  |  | 6+6+6+9+12 | 6+6+9+18+18 | 6+9+9+12+24 | 9+9+9+9+12 | 9+12+12+12+18 | 6+6+6+6+9+12 | 6+6+6+12+12+24 | 6+9+9+9+9+12 | 9+9+9+9+9+18
| 12+12 | 24+24 | 6+9+24 | 9+9+24 | 12+12+30 | 6+6+9+18 | 6+9+18+24 | 9+9+18+18 |  |  | 6+6+6+9+18 | 6+6+9+18+24 | 6+9+9+18+18 | 9+9+9+9+18 | 9+12+12+12+24 | 6+6+6+6+9+18 | 6+6+9+9+9+9 | 6+9+9+9+9+18 | 9+9+9+9+9+24
| 12+18 | 24+30 | 6+9+30 | 9+9+30 | 12+12+36 | 6+6+9+24 | 6+12+12+12 | 9+9+18+24 |  |  | 6+6+6+9+24 | 6+6+12+12+12 | 6+9+9+18+24 | 9+9+9+9+24 | 9+12+12+18+18 | 6+6+6+6+9+24 | 6+6+9+9+9+12 | 6+9+9+9+9+24 | 9+9+9+9+12+12
| 24+36 |  | 6+9+36 | 9+9+36 | 12+18+18 | 6+6+12+12 | 6+12+12+18 | 9+12+12+12 |  |  | 6+6+6+12+12 | 6+6+12+12+18 | 6+9+12+12+12 | 9+9+9+12+12 | 12+12+12+12+12 | 6+6+6+6+12+12 | 6+6+9+9+9+18 | 6+9+9+9+12+12 | 9+9+9+9+12+18
|  |  | 6+12+12 | 9+12+12 | 12+18+24 | 6+6+12+18 | 6+12+12+24 | 9+12+12+18 |  |  | 6+6+6+12+18 | 6+6+12+12+24 | 6+9+12+12+18 | 9+9+9+12+18 | 12+12+12+12+18 | 6+6+6+6+12+18 | 6+6+9+9+9+24 | 6+9+9+9+12+18 | 9+9+9+9+12+24
|  |  | 6+12+18 | 9+12+18 | 12+18+30 | 6+6+12+24 | 6+12+18+18 | 9+12+12+24 |  |  | 6+6+6+12+24 | 6+6+12+18+18 | 6+9+12+12+24 | 9+9+9+12+24 | 12+12+12+12+24 | 6+6+6+6+12+24 | 6+6+9+9+12+12 | 6+9+9+9+12+24 | 9+9+9+12+12+12
|  |  | 6+12+24 | 9+12+24 | 12+18+36 | 6+6+18+18 | 6+12+18+24 | 9+12+18+18 |  |  | 6+6+6+18+18 | 6+6+12+18+24 | 6+9+12+18+18 | 9+9+9+18+18 | 12+12+12+18+18 | 6+6+6+9+9+9 | 6+6+9+9+12+18 | 6+9+9+12+12+12 | 9+9+9+12+12+18
|  |  | 6+12+30 | 9+12+30 | 18+18+18 | 6+6+18+24 | 6+18+18+18 | 9+12+18+24 |  |  | 6+6+6+18+24 | 6+6+18+18+18 | 6+9+12+18+24 | 9+9+9+18+24 |  | 6+6+6+9+9+12 | 6+6+9+9+12+24 | 6+9+9+12+12+18 | 9+9+12+12+12+12
|  |  | 6+12+36 | 9+12+36 |  | 6+9+9+9 | 6+18+18+24 | 9+18+18+18 |  |  | 6+6+9+9+9 | 6+6+18+18+24 | 6+9+18+18+18 | 9+9+12+12+12 |  | 6+6+6+9+9+18 | 6+6+9+12+12+12 | 6+9+9+12+12+24 | 9+9+12+12+12+18
A Proud Member of the Carrier Family
*Approved connected combinations, reference product data for official connected heating and cooling capacities | [16 empty] | ©2025 Carrier. All rights reserved.
For Deluxe 6K/9K/12K high wall indoor units, they are considered as 18K unit in the multi-zone combination. (Same chassis with mid tier 18K High wall) | [16 empty] | ENERGY STAR® is a registered trademark of the U.S. EPA.
For Deluxe 18K high wall indoor units, they are considered as 24K unit in the multi-zone combination. (Same chassis size with mid tier 24K High wall) | [16 empty] | DLS-050-CP-00 ¦ 02/2025

## Crossover Solutions
Crossover Solutions Quick Reference Guide | [14 empty] | Ductless Systems
Indoor Unit With Factory Installed 24V Interface | Outdoor Unit With Base Pan Heater | AHRI Rated Btu's Cooling @ 95F [35C] Heating @ 47F [6.3C] | SEER2 | EER2 | HSPF2 | Energy Star v6.1 Certified | Line Set Liquid x Suction | Max. Line Length | Additional Charge ≥ 25ft | Max. Lift | MCA/MOCP | Max Heating Capacity BTU's At 70F [21.1C] Indoor DB @ Max CFM |  |  | Maximum Cooling BTU's At 80F [26.7C] Indoor DB @ Max CFM
[12 empty] | @-22F [-30C] | @-4F [-20C] | @5F [-15C] | @110F [43C] | @122F [50C]
This sheet is not intended to replace the installation instructions. It is a reference guide only. Always read through the installation instructions.
Quietcomfort Horizontal Discharge AHU 1:1 Quietcomfort Heat Pump Systems (Crossover Solutions)
D5FUHAH24XAK | D5CUHAH18AAK | 18,000/18,000 | 19 | 12.5 | 10.2 | YES | 3/8" x 3/4" | 98.42' | .70 Oz/ft | 65.62' | 16A / 20A | 11928 | 16514 | 19261 | 17916 | 14214
D5FUHAH24XAK | D5CUHAH24AAK | 24,000/24,000 | 18.7 | 12 | 10 | YES | 3/8" x 3/4" | 164.04' | .70 Oz/ft | 82.02' | 19A / 20A | 12297 | 17927 | 21458 | 23751 | 17725
D5FUHAH36XAK | D5CUHAH30AAK | 30,000/33,000 | 17.2 | 12.1 | 10.8 | YES | 3/8" x 3/4" | 164.04' | .70 Oz/ft | 82.02' | 29.5A / 30A | 18551 | 27252 | 33236 | 32779 | 20649
D5FUHAH36XAK | D5CUHAH36AAK | 36,000/37,000 | 18 | 12 | 10 | YES | 3/8" x 3/4" | 246' | .70 Oz/ft | 98.43' | 29A / 30A | 27729 | 37170 | 38436 | 38525 | 24495
D5FUHAH60XAK | D5CUHAH48AAK | 48,000/48,000 | 17.5 | 12 | 9.5 | YES | 3/8" x 3/4" | 246' | .70 Oz/ft | 98.43' | 38A / 40A | 30363 | 43387 | 48328 | 45560 | 32789
D5FUHAH60XAK | D5CUHAH60AAK | 54,000/55,000 | 17.5 | 12 | 9.5 | YES | 3/8" x 3/4" | 246' | .70 Oz/ft | 98.43' | 40A / 40A | 37307 | 49989 | 56830 | 53125 | 33738
Performance Horizontal Discharge AHU 1:1 Performance Heat Pump Systems (Crossover Solutions)
D5FUAAH18XAK | D5CUHAH18AAK | 18,000/19,000 | 19 | 12.5 | 9.8 | YES | 3/8" x 3/4" | 98.42' | .70 Oz/ft | 65.62' | 16A / 20A | 11229 | 16780 | 19813 | 18855 | 15316
D5FUAAH24XAK | D5CUHAH24AAK | 23,000/24,000 | 18.4 | 11.7 | 10 | YES | 3/8" x 3/4" | 164.04' | .70 Oz/ft | 82.02' | 19A / 20A | 12099 | 17309 | 22891 | 25051 | 16371
D5FUAAH30XAK | D5CUHAH30AAK | 30,000/34,000 | 16.9 | 11.7 | 10 | YES | 3/8" x 3/4" | 164.04' | .70 Oz/ft | 82.02' | 29.5A / 30A | 20066 | 28190 | 33287 | 32404 | 21287
D5FUAAH36XAK | D5CUHAH36AAK | 36,000/37,000 | 17.4 | 11.7 | 10.3 | YES | 3/8" x 3/4" | 246' | .70 Oz/ft | 98.43' | 29A / 30A | 27944 | 35662 | 41538 | 36996 | 24959
D5FUAAH48XAK | D5CUHAH48AAK | 48,000/50,000 | 16.5 | 10.5 | 9.5 | NO | 3/8" x 3/4" | 246' | .70 Oz/ft | 98.43' | 38A / 40A | 25870 | 40674 | 46850 | 42234 | 30465
D5FUAAH60XAK | D5CUHAH60AAK | 54,000/56,000 | 16 | 10 | 9 | NO | 3/8" x 3/4" | 246' | .70 Oz/ft | 98.43' | 40A / 40A | 30882 | 46714 | 54228 | 50848 | 34671
18k/24k IDU Capacity select via dip switch and must match ODU size
Performance Tier Horizontal Discharge AHU 1:1 Heat Pump Systems (Crossover Solutions)
D5FUAAH18XAK | D5CURAH18AAK | 18,000/18,000 | 18.8 | 11 | 9.2 | NO | 3/8" x 3/4" | 98.42' | .70 Oz/ft | 65.62' | 16A / 20A |  | 9175 | 11379 | 15815 | 9543
D5FUAAH24XAK | D5CURAH24AAK | 24,000/26,000 | 18.2 | 11 | 9.7 | NO | 3/8" x 3/4" | 164.04' | .70 Oz/ft | 82.02' | 19A / 20A |  | 16963 | 22433 | 24550 | 16043
D5FUAAH30XAK | D5CURAH30AAK | 30,000/31,000 | 17 | 10.8 | 8.5 | NO | 3/8" x 3/4" | 164.04' | .70 Oz/ft | 82.02' | 22.5A / 25A |  | 15521 | 19356 | 29603 | 14498
D5FUAAH36XAK | D5CURAH36AAK | 36,000/36,000 | 16.2 | 10 | 8.7 | NO | 3/8" x 3/4" | 246' | .70 Oz/ft | 98.42' | 24A / 30A |  | 22765 | 26515 | 32032 | 18926
D5FUAAH48XAK | D5CURAH48AAK | 48,000/48,000 | 16 | 10 | 8.5 | NO | 3/8" x 3/4" | 246' | .70 Oz/ft | 98.42' | 36A / 40A |  | 35908 | 43152 | 42022 | 30316
D5FUAAH60XAK | D5CURAH60AAK | 54,000/54,000 | 15.2 | 8.7 | 8.4 | NO | 3/8" x 3/4" | 246' | .70 Oz/ft | 98.42' | 39A / 40A |  | 35597 | 41473 | 41858 | 32571
18k/24k IDU Capacity select via dip switch and must match ODU size
Accessory Electric Heater Kits for D5FSAA & D5FUAA | [8 empty] | Accessory Electric Heater Kits for D5FUHA
Model Number | Size Used With | Model Number |  |  |  | Size Used With |  |  | Model Number |  | Size Used With |  |  | Model Number |  | Size Used With
EHKMC05KN | 18k, 24k, 30k, 36k | EHKMC15KN |  |  |  | 24k, 30k, 36k, 48k, 60k |  |  | EHKMD05KN |  | 24k, 36k |  |  | EHKMD15KN |  | 24k, 36k, 60k
EHKMC08KN | 18k, 24k, 30k, 36k, 48k | EHKMC20KN |  |  |  | 36k, 48k, 60k |  |  | EHKMD08KN |  | 24k, 36k |  |  | EHKMD20KN |  | 36k, 60k
EHKMC10KN | 18k, 24k, 30k, 36k, 48k, 60k | EHKMC25KN |  |  |  | 60k |  |  | EHKMD10KN |  | 24k, 36k, 60k |  |  | EHKMD25KN |  | 60k
Installation Note: A separate power supply is required for an Auxiliary Electric Heater. Do not power the electric heater directly from the outdoor unit. Always follow recommendations on the installation guide
System Installation Notes:
*The D5FUAA, D5FUHA, D5CUHA, D5CURA systems are powered seperately. The data supplied from MCA/MOCP is for the outdoor unit.
The minimum line length for all systems is 10'
D5FUAA/D5FUHA systems allow for either Non-Polarity RS485 or 24V Communication. Refer to the system's Product Data for more information on required wiring depending on communication style.
D5FUAA/D5FUHA air handlers require the use of a 3/8" bi-flow liquid line filter drier. The use of filter driers is not allowed on any other ductless style system.
Warranty Information
Residential & Multi-Family Applications: 10 year limited warranty to original purchaser on compressor and parts when system is *registered within 90-days of installation. *Registration not required in CA and Quebec .
ICP No Hassle Warranty: QuietComfort Series crossover units qualify for No Hassle Warranty. See warranty certificate for full details and exclusions.
Commercial Applications: 7 year limited warranty to original purchaser on compressor and parts. See Warranty documents for full details
A Proud Member of the Carrier Family
©2025 Carrier. All rights reserved.
ENERGY STAR® is a registered trademark of the U.S. EPA.
DLS-050-CP-00 ¦ 02/2025

## Multi-Zone IDU Pairings (hidden)
| High Wall |  |  | Ceiling Cassettes |  | Slim Ducted |  | Floor | Underceiling | Multi-Poise AHU
Btu/hr | Deluxe | Quietcomfort | Performance | 4-Way | 1-Way | Regular | High Static | Console | Console |  | Btu/hr
6K | D5FPHAH06XAK | D5FSHAH06XAK | - | - | D5FSOAH06XAK | D5FSDAH06XAK | - | - | - | - | 6K
9K | D5FPHAH09XAK | D5FSHAH09XAK | - | D5FSCAH12XAK | - | D5FSDAH12XAK | D5CSHAH12AAK | D5FSFAH09XAK | - | - | 9K
12K | D5FPHAH12XAK | D5FSHAH12XAK | - | D5FSCAH12XAK | D5FSOAH12XAK | D5FSDAH12XAK | D5CSHAH12AAK | D5FSFAH12XAK | - | - | 12K
18K | D5FPHAH18XAK | D5FSHAH18XAK | - | D5FSCAH18XAK | D5FSOAH18XAK | D5FSDAH18XAK | D5CSHAH18AAK | D5FSFAH16XAK | D5FCFAH18XAK | D5FSAAH18XBK | 18K
24K | - | D5FSHAH24XAK | - | D5FSCAH24XAK | - | - | D5CSHAH24AAK | - | D5FCFAH24XAK | D5FSAAH24XBK | 24K
30K | - | D5FSHAH30XAK | - | - | - | - | - | - | - | D5FSAAH30XBK | 30K
33K | - | D5FSHAH33XAK | - | - | - | - | - | - | - | - | 33K
36K | - | D5FSHAH36XAK | - | - | - | - | D5CLHAH36AAK | - | - | D5FSAAH36XBK | 36K

## Version Tracking
Version | Date Published | Changes Made
ICP DLS QRG Preliminary | 2024-09-27 | Initial Upload
ICP DLS QRG Preliminary V2 | 2025-02-07 | Standardization of table design across Single Zone DLS, Ducted, and Multi-Zone DLS Heating and Cooling Capacity ratings standardized by Outdoor and Indoor Bulb specifications New expanded capacity ranges include -22/-4/5 for heating Multizone Heat Pump heating and cooling capacities changed to mixed ducted/non-ducted Max CFM addition for Heating and Cooling Capacities Addition of High Static Ducted compatibility for MZ HPs Energy Star v6.1 Certification added Moved D5FSAA to Single Zone DLS Page Deluxe High Wall Multizone compatibility notes added Added Part Number (DLS-050-CP-00) Version Tracking Added